## input
! Comment line to describe the system - to be inputted
C 0 ! COMP
V 0 T_Suc_Sat 0 i 35 ! Compressor suction saturation T [F]
V 1 T_Dis_Sat 0 t 110 ! Compressor discharge saturation T [F]
V 2 H_Suc 0 r 185.282 ! Compressor suction H [Btu/lbm]
V 3 H_Dis 0 r 205.111 ! Compressor discharge H [Btu/lbm]
V 4 Mr 0 i 50 ! Compressor mass flow rate [lbm/h]
V 5 Power 0 r 322.871 ! Compressor power [W]
V 6 Power_Adj 0 i 1 ! Compressor power multiplier [-]
V 7 Mr_Adj 0 i 1 ! Compressor flow rate multiplier [-]
V 8 Heat_Gain_Ratio 0 i 0.9 ! Compressor heat gain ratio [-]
V 9 P_suc 0 r 122.019 ! Compressor suction pressure [psia]
V 10 P_dis 0 r 380.058 ! Compressor discharge pressure [psia]
V 11 Mr_adj_sup 0 r 1.01313 ! Compressor flow rate multiplier [-] | considering differed suction state
V 12 Superheat 0 i 15 ! superheat dgree | positive-superheat | negative-quality
V 13 S_suc 0 r 0.439478 ! compressor suction entropy | [Btu/lb/F]
V 14 H_dis_s 0 r 199.411 ! isentropic discharge enthalpy | [Btu/lb/F]
V 15 VOL_suc 0 r 0.525817 ! suction specific volume [ft^3/lb]
V 16 DISPLACEVOL 0 i 0.000501302 ! displacement volume | [ft^3]
V 17 RPM 0 g 1021 ! rotational speed | [rpm]
V 18 ETA_S 0 t 0.641299 ! isentropic efficiency | with assuming zero shell loss ratio [-]
V 19 ETA_V 0 t 0.85611 ! volumetric efficiency | [-]
V 20 dischargTemp 0 r 176.268 ! discharge temperature [F]
V 21 PRESSURE_RATIO 0 o 3.11475 ! compression pressure ratio | [-]
V 22 SuctTemp 0 o 50 ! suction temperature | [F]
V 23 POLYN 0 o 5.08117 ! Polytropic compression number [-]
V 24 ISENTROPICN 0 o 1.12117 ! Isentropic compression number [-]
M 0 NNN 0 r 0.85611 ! NNN
M 1 NNN 0 r 0.641299 ! NNN
C 1 ! CondFan
V 0 mass_flow_rate 0 r 1575.92 ! mass flow rate [lbm/h]; for air | it is dry air mass flow
V 1 HEAD 0 t 0.00838477 ! static head | [inH2O] for air stream
V 2 Tin 0 g 106.589 ! entering fluid temperature | [F]
V 3 Tout 0 r 106.6 ! exit fluid temperature | [F]
V 4 vol_flow_rate_in 0 g 23296.7 ! ent volumetric flow rate | [ft^3/h]
V 5 Power 0 g 1.28107 ! Power consumption | [W]
V 6 PIN 0 g 14.6 ! entering pressure | [psia]
V 7 POUT 0 r 14.6003 ! exit pressure | [psia]
V 8 Conc 0 g 0.0178791 ! entering mixture fraction | for example | specific humdity of air | [lbh20/lbda]
V 9 vol_flow_rate_out 0 g 23296.7 ! ext volumetric flow rate | [ft^3/h]
V 10 TWB 0 o 81.5153 ! alternative air wet bulb input (attribute-i): IF 0.0 < Input <0.05 | HUMIDITY RATIO; IF 0.05<=Input<=1 | RELATIVE HUMIDITY; IF >1 or =<0 | WET BULB TEMP OF AIR ENTERING THE HEAT EXCHANGER (F)
V 11 TWBo 0 o 300.66 ! exit wet bulb temperature [F]
V 12 HIN 0 r 45.4705 ! inlet fluid enthalpy [Btu/lbm]
V 13 HOUT 0 r 45.4733 ! outlet fluid enthalpy [Btu/lbm]
V 14 Power_Adj 0 i 1 ! Power multiplier [-]
V 15 DP_Adj 0 i 1 ! static head multiplier multiplier [-]
V 16 flow_Adj 0 i 1 ! flow rate multiplier [-]
V 17 RPM 0 i 1500 ! blade rotational speed [RPM]
V 18 EFFICIENCY 0 i 0.3 ! fan or pump efficiency [-]
V 19 VOLP1000 0 g 258.852 ! volumetric flow rate per 1000 RPM [cfm] or [gpm]
V 20 Hper1000 0 g 0.00374173 ! Head per 1000 RPM; [inH2O] for air; psiD for coolant
C 2 ! DischargeLine
V 0 MR 0 r 50 ! refrigerant mass flow rate [lb/h]
V 1 H_in 0 r 205.111 ! entering enthalpy | [Btu/h]
V 2 H_out 0 r 203.192 ! exit enthalpy | [Btu/h]
V 3 P_in 0 r 380.058 ! inlet pressure | psi
V 4 P_out 0 r 379.058 ! exit pressure | psi
V 5 DP 0 i 1 ! pressure drop [psid]
V 6 DH 0 r 1.91902 ! enthalpy change [btu/lb]
V 7 DQ 0 r 95.9508 ! line heat transfer rate | [btu/hr]
V 8 DP_Adj 0 r 450.823 ! Pressure drop multiplier [-]
V 9 DT 0 i 4.05 ! reference temperature drop at single phase specific heat | [R]
V 10 CHARG 0 o 0.0134961 ! charge mass | [lbm]
V 11 VOL_IN 0 o 9.84115 ! entering volumeric flow rate [ft^3/hr]
V 12 VOL_OUT 0 o 9.6451 ! leaving volumeric flow rate [ft^3/hr]
V 13 V_IN 0 o 2.63659 ! entering flow velocity [ft/s]
V 14 V_OUT 0 o 2.58407 ! leaving flow velocity [ft/s]
M 0 NNN 0 r 8.87265e-07 ! NNN
M 1 NNN 0 r 0.473831 ! NNN
C 3 ! Condenser
V 0 TSIN 0 r 109.801 ! entering saturation temp [F] | if super-critical | it is the same as the inlet pressure
V 1 HIN 0 r 203.192 ! entering enthalpy [btu/lb]
V 2 HOUT 0 r 112.407 ! exit enthalpy [Btu/lb]
V 3 MR 0 r 50 ! refrigerant mass flow rate [lb/h]
V 4 A_V 0 r 0.085 ! vapor phase area
V 5 A_TP 0 r 0.515 ! two-phase area
V 6 A_L 0 r 0.4 ! liquid phase area
V 7 Q_V 0 r 1043.72 ! vapor phase heat transfer rate [Btu/h]
V 8 Q_TP 0 r 3271.6 ! two-phase heat transfer rate [Btu/h]
V 9 Q_L 0 r 223.962 ! liquid phase heat transfer rate [Btu/h]
V 10 DP_R 0 r 0.0135851 ! refrigerant side DP [pisd]
V 11 CHARGE 0 r 2.00039 ! charge mass [lbm]
V 12 AIR_FLOW_RATE 0 r 1575.92 ! working fluid mass flow rate [lb/hr]
V 13 DP_AIR 0 r 0.00838477 ! fluid dp; if air [inH2O]; else [psiD]
V 14 TO_AIR 0 r 106.589 ! fluid exit temperature [F]
V 15 TI_AIR 0 i 95 ! fluid entering temperature [F]
V 16 HUMI 0 t 0.0178791 ! fluid entering concentration or air specific humidity
V 17 P_ATM 0 i 14.6 ! fluild pressure [psia]; if air - atmospheric pressure
V 18 POUT 0 r 379.045 ! refrigerant exit pressure [psia]
V 19 PIN 0 r 379.058 ! refrigerant entering pressure [psia]
V 20 Q_TOT 0 r 4542.26 ! total heat transfer rate [Btu/h]
V 21 SPEC_EXT 0 i 10 ! exit subcooling | superheat dgree [F] or quality | quality is minus | if supercritical | the exit temp
V 22 SHR 0 o 1 ! coil sensible heat tranfer ratio with no adjustment | output only
V 23 HUMO 0 r 0.0178791 ! fluid exit concentration; if air - specific humidity
V 24 HODRY 0 o 7.36951 ! fluid side dry heat transfer coefficient
V 25 HOWET 0 o 7.36951 ! fluid side wet (or subcooler) heat transfer coefficient
V 26 UAV 0 o 40.383 ! vapor phase UA
V 27 UATP 0 o 863.589 ! two-phase UA
V 28 UAL 0 o 52.6108 ! liquid-phase UA
V 29 UAo_TOT 0 o 2076.44 ! total air side UA
V 30 Rhin 0 o 0.5 ! inlet relative humidity [-]
V 31 Rhout 0 o 0.35313 ! outlet relative humidity [-]
V 32 CONC 0 o -1 ! refrigerant mixture concentration [0 to 1]
V 33 TWB 0 i 0.5 ! IF 0.05<=Input<=1 | RELATIVE HUMIDITY
V 34 TDBREF 0 o 80 ! reference dry bulb temprerature for curve-fit functions (F)
V 35 TWBREF 0 o 67 ! reference wet bulb temprerature for curve-fit functions (F)
V 36 TREFOUT 0 o 99.437 ! exit refrigerant temperature [F])
V 37 Rhoin 0 o 0.0690592 ! inlet air density [lbm/ft^3])
V 38 Rhoout 0 o 0.067607 ! outlet air density [lbm/ft^3])
V 39 TWBo 0 o 81.5153 ! exit air wet bulb temprerature [F]
V 40 SCFM 0 o 349.433 ! air flow [SCFM])
V 41 Vair_out 0 o 388.501 ! exit volumetric air flow rate [cfm])
V 42 DPheader 0 o 0 ! gas header pressure drop [psiD]
V 43 DPtot 0 o 0.0134947 ! total heat exchanger pressure drop [psiD]
V 44 TREFIN 0 o 169.523 ! entering refrigerant temperature [F])
V 45 InVol 0 o 0.0500876 ! total inner volume [ft^3]
V 46 M_V 0 o 0.0267397 ! vapor phase charge [lbm]
V 47 M_TP 0 o 0.699232 ! two-phase charge [lbm]
V 48 M_LIQ 0 o 1.27564 ! liquid-phase charge [lbm]
V 49 Cp_fluid 0 o 0.248557 ! average specific heat of single-phase fluid | e.g. air [Btu/F/lbm]
V 50 TDBREF1 0 o 80 ! secondary reference dry bulb temprerature for curve-fit functions (F)
V 51 TWBREF1 0 o 67 ! secondary reference wet bulb temprerature for curve-fit functions (F)
V 52 Afront 0 o 6.22243 ! frontal flow area [ft^2]
V 53 ASprimary 0 o 10.2423 ! primary surface area [ft^2]
V 54 ASsecond 0 o 319.327 ! secondary surface area [ft^2]
V 55 BYPASSFLRATIO 0 i 0 ! bypass flow ratio [-]
V 56 BYPASSFAC 0 o 0 ! bypass factor [-]
V 57 TubeWeight 0 o 0 ! Tube weight [lbm]
V 58 FinWeight 0 o 0 ! Fin weight [lbm]
V 59 TotFinWeight 0 o 0 ! Total Fin weight with No holes [lbm]
M 0 NNN 0 r 2.09425 ! NNN
M 1 NNN 0 r 1.09408 ! NNN
M 2 NNN 0 r 0.0970145 ! NNN
M 3 NNN 0 r 0.153976 ! NNN
M 4 NNN 0 r 829.597 ! NNN
M 5 NNN 0 r 433.401 ! NNN
M 6 NNN 0 r 38.4305 ! NNN
M 7 NNN 0 r 60.9948 ! NNN
M 8 NNN 0 r 5.39788e-06 ! NNN
M 9 NNN 0 r 3.37614e-09 ! NNN
M 10 NNN 0 r -0.156708 ! NNN
M 11 NNN 0 r -0.1403 ! NNN
M 12 NNN 0 r 0.24854 ! NNN
M 13 NNN 0 r 0.314585 ! NNN
M 14 NNN 0 r 1.35773 ! NNN
M 15 NNN 0 r 3.18911 ! NNN
M 16 NNN 0 r 4.44089e-16 ! NNN
M 17 NNN 0 r 1 ! NNN
C 4 ! LiquidLine
V 0 MR 0 r 50 ! refrigerant mass flow rate [lb/h]
V 1 H_in 0 r 112.407 ! entering enthalpy | [Btu/h]
V 2 H_out 0 r 112.407 ! exit enthalpy | [Btu/h]
V 3 P_in 0 r 379.045 ! inlet pressure | psi
V 4 P_out 0 r 378.045 ! exit pressure | psi
V 5 DP 0 i 1 ! pressure drop [psid]
V 6 DH 0 r 0 ! enthalpy change [btu/lb]
V 7 DQ 0 r 0 ! line heat transfer rate | [btu/hr]
V 8 DP_Adj 0 r 15.8867 ! Pressure drop multiplier [-]
V 9 DT 0 i 0 ! reference temperature drop at single phase specific heat | [R]
V 10 CHARG 0 o 3.27421 ! charge mass | [lbm]
V 11 VOL_IN 0 o 0.804744 ! entering volumeric flow rate [ft^3/hr]
V 12 VOL_OUT 0 o 0.804806 ! leaving volumeric flow rate [ft^3/hr]
V 13 V_IN 0 o 0.423747 ! entering flow velocity [ft/s]
V 14 V_OUT 0 o 0.42378 ! leaving flow velocity [ft/s]
M 0 NNN 0 r 2.51783e-05 ! NNN
M 1 NNN 0 r 0.480669 ! NNN
C 5 ! RefrCapacity
V 0 RefrCapacity 0 o 3643.76 ! result of the equation
C 6 ! TotPower
V 0 TotPower 0 o 324.152 ! result of the equation
C 7 ! EER
V 0 EER 0 o 11.2409 ! result of the equation
C 8 ! FanHead
V 0 FanHead 0 o 0.00838477 ! result of the equation
C 9 ! DisSatT
V 0 DisSatT 0 o 110 ! result of the equation
C 10 ! LiqT
V 0 LiqT 0 o 99.437 ! result of the equation