## input
! Comment line to describe the system - to be inputted
C 0 ! COMP
V 0 T_Suc_Sat 0 g 31.6683 ! Compressor suction saturation T [F]
V 1 T_Dis_Sat 0 g 104.953 ! Compressor discharge saturation T [F]
V 2 H_Suc 0 r 199.486 ! Compressor suction H [Btu/lbm]
V 3 H_Dis 0 r 214.974 ! Compressor discharge H [Btu/lbm]
V 4 Mr 0 r 504.034 ! Compressor mass flow rate [lbm/h]
V 5 Power 0 r 3268.44 ! Compressor power [W]
V 6 Power_Adj 0 i 1 ! Compressor power multiplier [-]
V 7 Mr_Adj 0 i 1 ! Compressor flow rate multiplier [-]
V 8 Heat_Gain_Ratio 0 i 0.7 ! Compressor heat gain ratio [-]
V 9 P_suc 0 r 105.166 ! Compressor suction pressure [psia]
V 10 P_dis 0 r 326.93 ! Compressor discharge pressure [psia]
V 11 Mr_adj_sup 0 r 1.03886 ! Compressor flow rate multiplier [-] | considering differed suction state
V 12 Superheat 0 i 5 ! superheat dgree | positive-superheat | negative-quality
V 13 S_suc 0 r 0.470499 ! compressor suction entropy | [Btu/lb/F]
V 14 H_dis_s 0 r 215.725 ! isentropic discharge enthalpy | [Btu/lb/F]
V 15 VOL_suc 0 r 0.691508 ! suction specific volume [ft^3/lb]
V 16 DISPLACEVOL 0 i 0.00164931 ! displacement volume | [ft^3]
V 17 RPM 0 i 3500 ! rotational speed | [rpm]
V 18 ETA_S 0 t 0.733994 ! isentropic efficiency | with assuming zero shell loss ratio [-]
V 19 ETA_V 0 t 1.00634 ! volumetric efficiency | [-]
V 20 dischargTemp 0 r 146.685 ! discharge temperature [F]
V 21 PRESSURE_RATIO 0 o 3.1087 ! compression pressure ratio | [-]
V 22 SuctTemp 0 o 36.6683 ! suction temperature | [F]
V 23 POLYN 0 o 2.62316 ! Polytropic compression number [-]
V 24 ISENTROPICN 0 o 1.13451 ! Isentropic compression number [-]
M 0 NNN 0 r 1.00634 ! NNN
M 1 NNN 0 r 0.733994 ! NNN
C 1 ! IndoorBlower
V 0 mass_flow_rate 0 i 10000 ! mass flow rate [lbm/h]; for air | it is dry air mass flow
V 1 DP 0 t 0.326162 ! static head | [inH2O] for air stream
V 2 Tin 0 g 91.3347 ! entering fluid temperature | [F]
V 3 Tout 0 r 91.963 ! exit fluid temperature | [F]
V 4 vol_flow_rate_in 0 g 140877 ! ent volumetric flow rate | [ft^3/h]
V 5 Power 0 g 450.181 ! Power consumption | [W]
V 6 PIN 0 g 14.696 ! entering pressure | [psia]
V 7 POUT 0 r 14.7078 ! exit pressure | [psia]
V 8 W 0 r 0.00879021 ! entering mixture fraction | for example | specific humdity of air | [lbh20/lbda]
V 9 vol_flow_rate_out 0 r 140924 ! ext volumetric flow rate | [ft^3/h]
V 10 TWB 0 o 67.0871 ! alternative air wet bulb input (attribute-i): IF 0.0 < Input <0.05 | HUMIDITY RATIO; IF 0.05<=Input<=1 | RELATIVE HUMIDITY; IF >1 or =<0 | WET BULB TEMP OF AIR ENTERING THE HEAT EXCHANGER (F)
V 11 TWBo 0 o 292.758 ! exit wet bulb temperature [F]
V 12 HIN 0 r 31.6563 ! inlet fluid enthalpy [Btu/lbm]
V 13 HOUT 0 r 31.8103 ! outlet fluid enthalpy [Btu/lbm]
V 14 Power_Adj 0 i 1 ! Power multiplier [-]
V 15 DP_Adj 0 i 1 ! static head multiplier multiplier [-]
V 16 flow_Adj 0 i 1 ! flow rate multiplier [-]
V 17 RPM 0 i 1140 ! blade rotational speed [RPM]
V 18 EFFICIENCY 0 i 0.2 ! fan or pump efficiency [-]
V 19 VOLP1000 0 g 2059.6 ! volumetric flow rate per 1000 RPM [cfm] or [gpm]
V 20 Hper1000 0 g 0.250971 ! Head per 1000 RPM; [inH2O] for air; psiD for coolant
V 21 STATSPEED 0 g 1200 ! stator speed [RPM]
M 0 NNN 0 r -99999 ! NNN
M 1 NNN 0 r -99999 ! NNN
M 2 NNN 0 r 0.95 ! NNN
M 3 NNN 0 r -99999 ! NNN
C 2 ! OutdoorFan
V 0 mass_flow_rate 0 r 20864.5 ! mass flow rate [lbm/h]; for air | it is dry air mass flow
V 1 DP 0 t 0.0468236 ! static head | [inH2O] for air stream
V 2 Tin 0 g 38.4553 ! entering fluid temperature | [F]
V 3 Tout 0 r 38.5643 ! exit fluid temperature | [F]
V 4 vol_flow_rate_in 0 i 264000 ! ent volumetric flow rate | [ft^3/h]
V 5 Power 0 g 161.476 ! Power consumption | [W]
V 6 PIN 0 g 14.696 ! entering pressure | [psia]
V 7 POUT 0 r 14.6977 ! exit pressure | [psia]
V 8 W 0 r 0.00469565 ! entering mixture fraction | for example | specific humdity of air | [lbh20/lbda]
V 9 vol_flow_rate_out 0 r 264027 ! ext volumetric flow rate | [ft^3/h]
V 10 TWB 0 o 37.9989 ! alternative air wet bulb input (attribute-i): IF 0.0 < Input <0.05 | HUMIDITY RATIO; IF 0.05<=Input<=1 | RELATIVE HUMIDITY; IF >1 or =<0 | WET BULB TEMP OF AIR ENTERING THE HEAT EXCHANGER (F)
V 11 TWBo 0 o 276.486 ! exit wet bulb temperature [F]
V 12 HIN 0 r 14.3067 ! inlet fluid enthalpy [Btu/lbm]
V 13 HOUT 0 r 14.3331 ! outlet fluid enthalpy [Btu/lbm]
V 14 Power_Adj 0 i 1 ! Power multiplier [-]
V 15 DP_Adj 0 i 1 ! static head multiplier multiplier [-]
V 16 flow_Adj 0 i 1 ! flow rate multiplier [-]
V 17 RPM 0 i 1140 ! blade rotational speed [RPM]
V 18 EFFICIENCY 0 i 0.15 ! fan or pump efficiency [-]
V 19 VOLP1000 0 g 3859.65 ! volumetric flow rate per 1000 RPM [cfm] or [gpm]
V 20 Hper1000 0 g 0.0360281 ! Head per 1000 RPM; [inH2O] for air; psiD for coolant
V 21 STATSPEED 0 g 1200 ! stator speed [RPM]
M 0 NNN 0 r -99999 ! NNN
M 1 NNN 0 r -99999 ! NNN
M 2 NNN 0 r 0.95 ! NNN
M 3 NNN 0 r -99999 ! NNN
C 3 ! DischargeLine
V 0 MR 0 r 504.034 ! refrigerant mass flow rate [lb/h]
V 1 H_in 0 r 214.974 ! entering enthalpy | [Btu/h]
V 2 H_out 0 r 214.133 ! exit enthalpy | [Btu/h]
V 3 P_in 0 r 326.93 ! inlet pressure | psi
V 4 P_out 0 r 325.367 ! exit pressure | psi
V 5 DP 0 r 1.56386 ! pressure drop [psid]
V 6 DH 0 r 0.841176 ! enthalpy change [btu/lb]
V 7 DQ 0 r 423.981 ! line heat transfer rate | [btu/hr]
V 8 DP_Adj 0 i 1 ! Pressure drop multiplier [-]
V 9 DT 0 i 2 ! reference temperature drop at single phase specific heat | [R]
V 10 CHARG 0 o 0.255575 ! charge mass | [lbm]
V 11 VOLin 0 o 124.553 ! entering volumeric flow rate [ft^3/hr]
V 12 VOLout 0 o 123.936 ! leaving volumeric flow rate [ft^3/hr]
V 13 Vin 0 o 13.7185 ! entering flow velocity [ft/s]
V 14 Vout 0 o 13.6505 ! leaving flow velocity [ft/s]
M 0 NNN 0 r 6.15574e-06 ! NNN
M 1 NNN 0 r 0.42065 ! NNN
C 4 ! SuctionLine
V 0 MR 0 r 504.034 ! refrigerant mass flow rate [lb/h]
V 1 H_in 0 r 198.937 ! entering enthalpy | [Btu/h]
V 2 H_out 0 r 199.486 ! exit enthalpy | [Btu/h]
V 3 P_in 0 r 106.73 ! inlet pressure | psi
V 4 P_out 0 r 105.166 ! exit pressure | psi
V 5 DP 0 r 1.56386 ! pressure drop [psid]
V 6 DH 0 r -0.549051 ! enthalpy change [btu/lb]
V 7 DQ 0 r -276.74 ! line heat transfer rate | [btu/hr]
V 8 DP_Adj 0 i 1 ! Pressure drop multiplier [-]
V 9 DT 0 i -2 ! reference temperature drop at single phase specific heat | [R]
V 10 CHARG 0 o 0.0921595 ! charge mass | [lbm]
V 11 VOLin 0 o 340.619 ! entering volumeric flow rate [ft^3/hr]
V 12 VOLout 0 o 348.543 ! leaving volumeric flow rate [ft^3/hr]
V 13 Vin 0 o 37.5164 ! entering flow velocity [ft/s]
V 14 Vout 0 o 38.3892 ! leaving flow velocity [ft/s]
M 0 NNN 0 r 6.15574e-06 ! NNN
M 1 NNN 0 r 0.274557 ! NNN
C 5 ! Condenser
V 0 TSIN 0 r 104.6 ! entering saturation temp [F] | if super-critical | it is the same as the inlet pressure
V 1 HIN 0 r 214.133 ! entering enthalpy [btu/lb]
V 2 HOUT 0 r 110.703 ! exit enthalpy [Btu/lb]
V 3 MR 0 r 504.034 ! refrigerant mass flow rate [lb/h]
V 4 A_V 0 r 0.121429 ! vapor phase area
V 5 A_TP 0 r 0.780952 ! two-phase area
V 6 A_L 0 r 0.097619 ! liquid phase area
V 7 Q_V 0 r 7071.88 ! vapor phase heat transfer rate [Btu/h]
V 8 Q_TP 0 r 42767.1 ! two-phase heat transfer rate [Btu/h]
V 9 Q_L 0 r 2293.23 ! liquid phase heat transfer rate [Btu/h]
V 10 DP_R 0 r 0.710712 ! refrigerant side DP [pisd]
V 11 CHARGE 0 r 2.99931 ! charge mass [lbm]
V 12 AIR_FLOW_RATE 0 r 10000 ! working fluid mass flow rate [lb/hr]
V 13 DP_AIR 0 r 0.126162 ! fluid dp; if air [inH2O]; else [psiD]
V 14 TO_AIR 0 r 91.3347 ! fluid exit temperature [F]
V 15 TI_AIR 0 i 70 ! fluid entering temperature [F]
V 16 HUMI 0 i 0.00879021 ! fluid entering concentration or air specific humidity
V 17 P_ATM 0 t 14.696 ! fluild pressure [psia]; if air - atmospheric pressure
V 18 POUT 0 r 324.655 ! refrigerant exit pressure [psia]
V 19 PIN 0 r 325.367 ! refrigerant entering pressure [psia]
V 20 Q_TOT 0 r 52132.2 ! total heat transfer rate [Btu/h]
V 21 SPEC_EXT 0 i 10 ! exit subcooling | superheat dgree [F] or quality | quality is minus | if supercritical | the exit temp
V 22 SHR 0 o 1 ! coil sensible heat tranfer ratio with no adjustment | output only
V 23 HUMO 0 r 0.00879021 ! fluid exit concentration; if air - specific humidity
V 24 HODRY 0 o 8.65483 ! fluid side dry heat transfer coefficient
V 25 HOWET 0 o 8.65483 ! fluid side wet (or subcooler) heat transfer coefficient
V 26 UAV 0 o 195.488 ! vapor phase UA
V 27 UATP 0 o 2115.53 ! two-phase UA
V 28 UAL 0 o 180.28 ! liquid-phase UA
V 29 UAo_TOT 0 o 3344.95 ! total air side UA
V 30 Rhin 0 o 0.563934 ! inlet relative humidity [-]
V 31 Rhout 0 o 0.281164 ! outlet relative humidity [-]
V 32 CONC 0 o -1 ! refrigerant mixture concentration [0 to 1]
V 33 TWB 0 i 60 ! WET BULB TEMP OF AIR ENTERING THE HEAT EXCHANGER [F]
V 34 TDBREF 0 o 80 ! reference dry bulb temprerature for curve-fit functions (F)
V 35 TWBREF 0 o 67 ! reference wet bulb temprerature for curve-fit functions (F)
V 36 TREFOUT 0 o 92.1024 ! exit refrigerant temperature [F])
V 37 Rhoin 0 o 0.0738431 ! inlet air density [lbm/ft^3])
V 38 Rhoout 0 o 0.0703747 ! outlet air density [lbm/ft^3])
V 39 TWBo 0 o 67.0871 ! exit air wet bulb temprerature [F]
V 40 SCFM 0 o 2217.32 ! air flow [SCFM])
V 41 Vair_out 0 o 2368.28 ! exit volumetric air flow rate [cfm])
V 42 DPheader 0 o 0 ! gas header pressure drop [psiD]
V 43 DPtot 0 o 0.711098 ! total heat exchanger pressure drop [psiD]
V 44 TREFIN 0 o 143.725 ! entering refrigerant temperature [F])
V 45 InVol 0 o 0.125536 ! total inner volume [ft^3]
V 46 M_V 0 o 0.0749982 ! vapor phase charge [lbm]
V 47 M_TP 0 o 2.14275 ! two-phase charge [lbm]
V 48 M_LIQ 0 o 0.782617 ! liquid-phase charge [lbm]
V 49 Cp_fluid 0 o 0.244415 ! average specific heat of single-phase fluid | e.g. air [Btu/F/lbm]
V 50 TDBREF1 0 o 80 ! secondary reference dry bulb temprerature for curve-fit functions (F)
V 51 TWBREF1 0 o 67 ! secondary reference wet bulb temprerature for curve-fit functions (F)
V 52 Afront 0 o 6.61133 ! frontal flow area [ft^2]
V 53 AsPrimary 0 o 22.3102 ! primary surface area [ft^2]
V 54 AsSecondary 0 o 421.281 ! secondary surface area [ft^2]
V 55 BYPASSFLRATIO 0 i 0 ! bypass flow ratio [-]
V 56 BYPASSFAC 0 o 0 ! bypass factor [-]
V 57 TubeWeight 0 o 0 ! Tube weight [lbm]
V 58 FinWeight 0 o 0 ! Fin weight [lbm]
V 59 TotFinWeight 0 o 0 ! Total Fin weight with No holes [lbm]
M 0 NNN 0 r 0.689216 ! NNN
M 1 NNN 0 r 0.647476 ! NNN
M 2 NNN 0 r 0.278548 ! NNN
M 3 NNN 0 r 0.288949 ! NNN
M 4 NNN 0 r 1683.92 ! NNN
M 5 NNN 0 r 1581.94 ! NNN
M 6 NNN 0 r 680.561 ! NNN
M 7 NNN 0 r 705.972 ! NNN
M 8 NNN 0 r 2.79905e-06 ! NNN
M 9 NNN 0 r 1.26162e-09 ! NNN
M 10 NNN 0 r -0.109491 ! NNN
M 11 NNN 0 r -0.143235 ! NNN
M 12 NNN 0 r 0.244354 ! NNN
M 13 NNN 0 r 0.617632 ! NNN
M 14 NNN 0 r 2.74377 ! NNN
M 15 NNN 0 r 8.01706 ! NNN
M 16 NNN 0 r 1.33227e-15 ! NNN
M 17 NNN 0 r 1 ! NNN
C 6 ! Evaporator
V 0 TSIN 0 r 39.4507 ! entering saturation temp [F] | if super-critical | it is the same as the inlet pressure
V 1 HIN 0 r 110.703 ! entering enthalpy [btu/lb]
V 2 HOUT 0 r 198.937 ! exit enthalpy [Btu/lb]
V 3 MR 0 r 504.034 ! refrigerant mass flow rate [lb/h]
V 4 A_V 0 r 0.0075 ! vapor phase area
V 5 A_TP 0 r 0.9925 ! two-phase area
V 6 A_L 0 r 0 ! liquid phase area
V 7 Q_V 0 r -269.724 ! vapor phase heat transfer rate [Btu/h]
V 8 Q_TP 0 r -44204.8 ! two-phase heat transfer rate [Btu/h]
V 9 Q_L 0 r 1.39424 ! liquid phase heat transfer rate [Btu/h]
V 10 DP_R 0 r 18.7229 ! refrigerant side DP [pisd]
V 11 CHARGE 0 r 3.46501 ! charge mass [lbm]
V 12 AIR_FLOW_RATE 0 r 20864.5 ! working fluid mass flow rate [lb/hr]
V 13 DP_AIR 0 r 0.0468236 ! fluid dp; if air [inH2O]; else [psiD]
V 14 TO_AIR 0 r 38.4553 ! fluid exit temperature [F]
V 15 TI_AIR 0 i 47 ! fluid entering temperature [F]
V 16 HUMI 0 t 0.00475017 ! fluid entering concentration or air specific humidity
V 17 P_ATM 0 i 14.696 ! fluild pressure [psia]; if air - atmospheric pressure
V 18 POUT 0 r 106.73 ! refrigerant exit pressure [psia]
V 19 PIN 0 r 125.475 ! refrigerant entering pressure [psia]
V 20 Q_TOT 0 r -44511.4 ! total heat transfer rate [Btu/h]
V 21 SPEC_EXT 0 g 2.71893 ! exit subcooling | superheat dgree [F] or quality | quality is minus | if supercritical | the exit temp
V 22 SHR 0 o 0.97289 ! coil sensible heat tranfer ratio with no adjustment | output only
V 23 HUMO 0 r 0.00469727 ! fluid exit concentration; if air - specific humidity
V 24 HODRY 0 o 10.2441 ! fluid side dry heat transfer coefficient
V 25 HOWET 0 o 9.31935 ! fluid side wet (or subcooler) heat transfer coefficient
V 26 UAV 0 o 35.508 ! vapor phase UA
V 27 UATP 0 o 9787.9 ! two-phase UA
V 28 UAL 0 o 0 ! liquid-phase UA
V 29 UAo_TOT 0 o 11232.4 ! total air side UA
V 30 Rhin 0 o 0.7 ! inlet relative humidity [-]
V 31 Rhout 0 o 0.961543 ! outlet relative humidity [-]
V 32 CONC 0 o -1 ! refrigerant mixture concentration [0 to 1]
V 33 TWB 0 i 0.7 ! IF 0.05<=Input<=1 | RELATIVE HUMIDITY
V 34 TDBREF 0 o 80 ! reference dry bulb temprerature for curve-fit functions (F)
V 35 TWBREF 0 o 67 ! reference wet bulb temprerature for curve-fit functions (F)
V 36 TREFOUT 0 o 35.3466 ! exit refrigerant temperature [F])
V 37 Rhoin 0 o 0.0776926 ! inlet air density [lbm/ft^3])
V 38 Rhoout 0 o 0.0787801 ! outlet air density [lbm/ft^3])
V 39 TWBo 0 o 38.0027 ! exit air wet bulb temprerature [F]
V 40 SCFM 0 o 4626.33 ! air flow [SCFM])
V 41 Vair_out 0 o 4414.08 ! exit volumetric air flow rate [cfm])
V 42 DPheader 0 o 0 ! gas header pressure drop [psiD]
V 43 DPtot 0 o 18.7454 ! total heat exchanger pressure drop [psiD]
V 44 TREFIN 0 o 39.7543 ! entering refrigerant temperature [F])
V 45 InVol 0 o 0.302411 ! total inner volume [ft^3]
V 46 M_V 0 o 0.00337031 ! vapor phase charge [lbm]
V 47 M_TP 0 o 3.4573 ! two-phase charge [lbm]
V 48 M_LIQ 0 o 0 ! liquid-phase charge [lbm]
V 49 Cp_fluid 0 o 0.242475 ! average specific heat of single-phase fluid | e.g. air [Btu/F/lbm]
V 50 TDBREF1 0 o 80 ! secondary reference dry bulb temprerature for curve-fit functions (F)
V 51 TWBREF1 0 o 67 ! secondary reference wet bulb temprerature for curve-fit functions (F)
V 52 Afront 0 o 23.8897 ! frontal flow area [ft^2]
V 53 AsPrimary 0 o 52.8776 ! primary surface area [ft^2]
V 54 AsSecondary 0 o 1232.32 ! secondary surface area [ft^2]
V 55 BYPASSFLRATIO 0 i 0 ! bypass flow ratio [-]
V 56 BYPASSFAC 0 o 0.0824409 ! bypass factor [-]
V 57 TubeWeight 0 o 0 ! Tube weight [lbm]
V 58 FinWeight 0 o 0 ! Fin weight [lbm]
V 59 TotFinWeight 0 o 0 ! Total Fin weight with No holes [lbm]
M 0 NNN 0 r 1.20377 ! NNN
M 1 NNN 0 r 1.13144 ! NNN
M 2 NNN 0 r 1.13144 ! NNN
M 3 NNN 0 r 1.17921 ! NNN
M 4 NNN 0 r 6264.54 ! NNN
M 5 NNN 0 r 5888.11 ! NNN
M 6 NNN 0 r 5888.11 ! NNN
M 7 NNN 0 r 6136.72 ! NNN
M 8 NNN 0 r 7.37863e-05 ! NNN
M 9 NNN 0 r 1.0756e-10 ! NNN
M 10 NNN 0 r -0.443912 ! NNN
M 11 NNN 0 r 21.7953 ! NNN
M 12 NNN 0 r 0.249457 ! NNN
M 13 NNN 0 r 0.449375 ! NNN
M 14 NNN 0 r 3.48343 ! NNN
M 15 NNN 0 r 20.4887 ! NNN
M 16 NNN 0 r 4.44089e-16 ! NNN
M 17 NNN 0 r 1 ! NNN
C 7 ! LiquidLine
V 0 MR 0 r 504.034 ! refrigerant mass flow rate [lb/h]
V 1 H_in 0 r 110.703 ! entering enthalpy | [Btu/h]
V 2 H_out 0 r 110.703 ! exit enthalpy | [Btu/h]
V 3 P_in 0 r 324.655 ! inlet pressure | psi
V 4 P_out 0 r 322.405 ! exit pressure | psi
V 5 DP 0 r 2.25005 ! pressure drop [psid]
V 6 DH 0 r 1.11873e-22 ! enthalpy change [btu/lb]
V 7 DQ 0 r 5.63882e-20 ! line heat transfer rate | [btu/hr]
V 8 DP_Adj 0 i 1 ! Pressure drop multiplier [-]
V 9 DT 0 i 0 ! reference temperature drop at single phase specific heat | [R]
V 10 CHARG 0 o 0.782502 ! charge mass | [lbm]
V 11 VOLin 0 o 8.502 ! entering volumeric flow rate [ft^3/hr]
V 12 VOLout 0 o 8.50305 ! leaving volumeric flow rate [ft^3/hr]
V 13 Vin 0 o 4.47683 ! entering flow velocity [ft/s]
V 14 Vout 0 o 4.47738 ! leaving flow velocity [ft/s]
M 0 NNN 0 r 8.85591e-06 ! NNN
M 1 NNN 0 r 0.473146 ! NNN
C 8 ! ChargSOLVER
V 0 DRIVEVAR 0 i 10 ! driving variable
V 1 RESULT 0 o -99999 ! result variable
C 9 ! ChargeFunc
V 0 SysCharge 0 o 7.59456 ! result of the equation
C 10 ! ODCFMCal
V 0 ODCFM 0 o 4400 ! result of the equation
C 11 ! IDCFMCal
V 0 IDCFM 0 o 2347.95 ! result of the equation
C 12 ! TotCapacityCal
V 0 TotCapacity 0 o 53668.2 ! result of the equation
C 13 ! TotPowCal
V 0 TotPow 0 o 3880.09 ! result of the equation
C 14 ! SHCOP
V 0 SHCOP 0 o 4.05383 ! result of the equation
C 15 ! ExtHead
V 0 ExtHead 0 o 0.326162 ! result of the equation